## C&F
Indoor Model |  |  | KSHF53HFAN1 | KSHF70HFAN1 | KSHF105HFAN3 | KSHF140HFAN3 | KSHE176HFAN3
Outdoor Model |  |  | KSUT53HFAN1 | KSUT70HFAN1 | KSUR105HFAN3 | KSUT140HFAN3 | KSUT176HFAN3
Power supply |  | V,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3 | 380~415,50,3
Cooling | Capacity | Btu/h | 18500 | 24000 | 36000 | 48000 | 55000
|  |  | 5.422 | 7.034 | 10.551 | 14.068 | 16.1196
| Input | W | 2110 | 2630 | 3505 | 5450 | 6400
| Current | A | 9.36 | 12.62 | 5.9 | 9.3 | 10.5
| EER | W/W | 2.5697 | 2.6745 | 3.01 | 2.58 | 2.52
Heating | Capacity | Btu/h | 19000 | 26000 | 38000 | 55000 | 60000
|  |  | 5.5686 | 7.6202 | 11.1372 | 16.1196 | 17.585
| Input | W | 1730 | 2450 | 3468 | 5080 | 5800
| Current | A | 7.67 | 11.76 | 5.8 | 8.6 | 9.6
| COP | W/W | 3.2188 | 3.1103 | 3.21 | 3.17 | 3.03
Indoor fan motor | Model |  | YKSS-55-4-27-1 | YKSS-55-4-27-1 | YKSS-125-4-5 | YKSS-85-4-1L-2 | YKSS-85-4-3
| Qty |  | 1 | 1 | 1 | 2 | 2
| Input | W | 125 | 125 | 148 | 166.0 | 120.0
| Capacitor | uF | 2 | 2.5 | 4.5 | 2.5 | 2.5
| Speed(Hi/Med/Lo) | r/min | 1310/1190/1040 | 1310/1190/1040 | 1370/1300/1225 | 1285/1205/1130 | 1310/1190/1080
Indoor coil | Number of rows |  | 2 | 2 | 2.0 | 3 | 3.0
| Tube pitch(a)x row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37
| Fin spacing | mm | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
| Fin type |  | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminum(Golden) | Hydrophilic aluminum(Golden)
| Tube outside dia.and type | mm | Ф7,innergroove tube | Ф7,innergroove tube | Φ7,Inner groove tube | Φ7,Inner groove tube | Φ7,Inner groove tube
| Coil length x height x width | mm | 795x294x26.74 | 795x294x26.74 | 935x294x26.74 | 1300*40.11*294 | 1300x294x40.11
| Number of circuits |  | 6 | 6 | 6 | 8 | 10
Indoor air flow(Hi/Med/Lo) |  | m3/h | 1150/950/800 | 1250/1050/900 | 1819/1536/1331 | 2350/2150/2000 | 2267/1846/1636
Indoor noise level (sound pressure)(Hi/Med/Lo) |  | dB(A) | 52/47/42 | 53/48/44 | 53/48.5/45 | 54.0/51.0/48.0 | 54.5/50.6/48.0
Throttle type |  |  | ― | ― | ― | ― | ―
Indoor unit | Dimension (WxDxH) | mm | 1068x675x235 | 1068x675x235 | 1285x675x235 | 1650x675x235 | 1650x675x235
| Packing (WxDxH) | mm | 1145x755x313 | 1145x755x313 | 1360x755x313 | 1725x755x318 | 1725x755x318
| Net/Gross weight | kg | 24/29 | 24.6/29.8 | 29.9/35.5 | 39/45 | 39/45
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5
Drainage water pipe diameter |  | mm | ODФ25 | ODФ25 | ODΦ25mm | ODΦ25mm | ODΦ25mm
Refrigerant piping | Liquid side/Gas side | mm(inch) | Φ6.35/Φ12.7(1/4"/1/2") | Φ9.52Φ15.9(3/8"/5/8") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4")
Controller |  |  | Remote control | Remote control | remote control | Remote control | Remote control
Operation temperature |  | ℃ | 17~30 | 17~30 | 17~30 | 17~30 | 17~30
Room temperature | Cooling | ℃ | 17~32 | 17~32 | 17～32 | 17~32 | 17~32
| Heating | ℃ | 0~30 | 0~30 | 0～30 | 0~30 | 0~30
Qty’per 20’ /40’ /40'HQ |  | Indoor | 102/220/252 | 102/220/252 | 92/188/213 | 72/147/167 | 72/147/167

## Cassette
|  |  | Compact Cassette |  | CASSETTE
Indoor model |  |  | KSZT35HFAN1 | KSZT53HFAN1 | KSVR70HFAN1 | KSVR105HFAN3 | KSVQ140HFAN3 | KSVQ176HFAN3
Outdoor model |  |  | KSUT35HFAN1 | KSUT53HFAN1 | KSUT70HFAN1 | KSUR105HFAN3 | KSUT140HFAN3 | KSUT176HFAN3
Power supply |  | V,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3 | 380~415,50,3
Cooling | Capacity | Btu/h | 12000 | 18300 | 24000 | 36000 | 48000 | 55000
| Input | W | 1095 | 1980 | 2600 | 3505 | 5191 | 6272
| Current | A | 4.8 | 8.78 | 12.48 | 5.9 | 9.2 | 11.0
| EER | W/W | 3.21 | 2.7088 | 2.71 | 3.01 | 2.71 | 2.57
Heating | Capacity | Btu/h | 13000 | 19000 | 26000 | 38000 | 52000 | 61000
| Input | W | 1250 | 1720 | 2400 | 3580 | 4763 | 5843
| Current | A | 5.3 | 7.63 | 11.52 | 6 | 8.5 | 10.3
| COP | W/W | 3.01 | 3.2375 | 3.18 | 3.11 | 3.2 | 3.06
Indoor fan motor | Model |  | YKT-17-6-6 | YKT-27-4-6 | YKT-42-6-6 | YKS-125-6-3 | YKS-125-6-3 | YKS-125-6-3
| Qty |  | 1 | 1 | 1 | 1 | 1 | 1
| Input | W | 40.5 | 86.7 | 81 | 174 | 174 | 174
| Capacitor | uF | 1.5 | 2 | 3.5 | 5 | 5 | 5
| Speed(Hi/Med/Lo) | r/min | 640/540/440 | 850/685/583 | 580/510/430 | 690/610/540 | 775/610/540 | 775/610/540
Indoor coil | Number of rows |  | 1 | 2 | 2 | 2 | 3 | 3
| Tube pitch(a)* row pitch(b) | mm | 21*13.37 | 21*13.37 | 21*13.37 | 21x13.37 | 21*13.37 | 21*13.37
| Fin spacing | mm | 1.3 | 1.3 | 1.4 | 1.4 | 1.4 | 1.4
| Fin type |  | Hydrophilic aluminium(Golden | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden)
| Tube outside dia.and type | mm | Φ7,innergroove tube | Φ7,innergroove tube | Φ7,innergroove tube | Φ7,Inner groove tube | Φ7,innergroove tube | Φ7,innergroove tube
| Coil length * height * width | mm | 1380*210*13.37 | 1360*210*26.74 | 2010*168*26.74 | 2010x210x26.74 | 2080*210*40.11 | 2080*252*40.11
| Number of circuits |  | 3 | 4 | 8 | 10 | 10 | 12
Indoor air flow (Hi/Mid/Lo) |  | m3/h | 607/504/413 | 810/650/530 | 1200/1050/900 | 1731/1494/1297 | 1990/1566/1305 | 1962/1541/1357
Indoor noise level (sound pressure) (Hi/Mid/Lo) |  | dB(A) | 42/38/35 | 48/41/36 | 48/44/39 | 51/48/45.5 | 54/48/45 | 53/47/46
Throttle type |  |  | ― | ― | ― | ― | ― | ―
Indoor unit | Dimension (W*D*H)(body) | mm | 570*570*260 | 570*570*260 | 840*840*205 | 840*840*245 | 840*840*245 | 840*840*287
| Packing (W*D*H)(body) | mm | 655*655*290 | 655*655*290 | 900*900*225 | 900*900*265 | 900*900*265 | 900*900*292
| Dimension (W*D*H)(panel) | mm | 647*647*50 | 647*647*50 | 950*950*55 | 950*950*55 | 950*950*55 | 950*950*55
| Packing (W*D*H)(panel) | mm | 715*715*123 | 715*715*123 | 1035*1035*90 | 1035*1035*90 | 1035*1035*90 | 1035*1035*90
| Net/Gross weight(body) | kg | 14.5/17.5 | 16.5/19 | 22.1/25.5 | 24.9/28.8 | 27/32 | 29/34
| Net/Gross weight(panel) | kg | 2.5/4.5 | 2.5/4.5 | 5/8 | 5/8 | 5/8 | 5/8
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5
Drainage water pipe diameter |  | mm | ODΦ25 | ODΦ25 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32
Refrigerant piping | Liquid side/Gas side | mm | Φ6.35/Φ12.7(1/4"/1/2") | Φ6.35/Φ12.7(1/4"/1/2") | Φ9.52/Φ15.9(3/8"/5/8") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4")
Controller |  |  | Remote control | Remote control | Remote control | Remote control | Remote control | Remote control
Operation temperature |  | ℃ | 17~30 | 17~30 | 17~30 | 17~30 | 17~30 | 17~30
Room temperature | Cooling | ℃ | 17~32 | 17~32 | 17~32 | 17～32 | 17~32 | 17~32
| Heating | ℃ | 0~30 | 0~30 | 0~30 | 0～30 | 0~30 | 0~30
Qty’per 20’ /40’ /40'HQ |  | Indoor | 234/488/566 | 234/488/566 | 148/312/342 | 128/268/294 | 128/268/294 | 100/212/238
Remarks:1.The above design and specifications are subject to change without prior notice for product improvement.

## Duct
Indoor model |  |  | KSKS53HFAN1 | KSKS70HFAN1 | KSKR105HFAN3 | KSKR140HFAN3 | KSKR176HFAN3
Outdoor model |  |  | KSUT53HFAN1 | KSUT70HFAN1 | KSUR105HFAN3 | KSUT140HFAN3 | KSUT176HFAN3
Power supply |  | V,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3 | 380~415,50,3
Cooling | Capacity | Btu/h | 18000 | 24000 | 36000 | 48000 | 55000
| Input | W | 2200 | 2870 | 3505 | 5350 | 6360
| Current | A | 9.7 | 13.5 | 5.9 | 9.2 | 11
| EER | W/W | 2.4 | 2.45 | 3.01 | 2.63 | 2.53
Heating | Capacity | Btu/h | 19000 | 26000 | 40000 | 55000 | 60000
| Input | W | 1750 | 2300 | 3435 | 4815 | 5540
| Current | A | 7.9 | 11.3 | 5.7 | 8.3 | 9.3
| COP | W/W | 3.18 | 3.31 | 3.41 | 3.35 | 3.17
Indoor fan motor | Model |  | YKSS-74-4-16-1 | YKSS-115-4-21 | YKSS-115-4-21 | YKSS-210-4-2 | YKSS-210-4-2
| Qty |  | 1 | 1 | 1 | 1 | 1
| Input | W | 163 | 253 | 253 | 430.0 | 430.0
| Capacitor | uF | 3.5 | 5 | 8 | 10 | 10
| Speed(Hi/Med/Lo) | r/min | 1000/750/680 | 860/830/730 | 990/876/787 | 940/850/740/645 | 940/850/740/645
Indoor coil | Number of rows |  | 3 | 3 | 3 | 3.0 | 3.0
| Tube pitch(a)*row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37
| Fin spacing | mm | 1.4 | 1.4 | 1.4 | 1.3 | 1.3
| Fin type |  | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminum(Golden) | Hydrophilic aluminum(Golden)
| Tube outside dia.and type | mm | Ф7,innergroove tube | Ф7,innergroove tube | Φ7,Inner groove tube | Φ7,Inner groove tube | Φ7,Inner groove tube
| Coil length×height×width | mm | 695x252x40.11 | 915x294x40.11 | 915x294x40.11 | 1030x378x40.11 | 1030x378x40.11
| Number of circuits |  | 4 | 7 | 7 | 8 | 8
Indoor air flow (Hi/Med/Lo) |  | m3/h | 980/815/730 | 1360/1177/965 | 1804/1372/1149 | 2150/1800/1400 | 2400/1850/1490
ESP | Rated | Pa | 25 | 25 | 37 | 50 | 50
| Range | Pa | 0-100 | 0-160 | 0-160 | 0-160 | 0-160
Indoor noise level (Hi/Med/Lo) |  | dB(A) | 44.4/42.1/39.5 | 43.6/40.5/37.9 | 47/40.5/38 | 48.0/45.0/42.0 | 51.7/46.9/44.4
Throttle type |  |  | / | / | / | 1200x874x300 | 1200x874x300
Indoor unit | Dimension (WxDxH) | mm | 880×674×210 | 1100×774×249 | 1100x774x249 | 1405x915x365 | 1405x915x365
| Packing(WxDxH) | mm | 1070×725×270 | 1305×805×305 | 1305x805x305 | 46/54.5 | 46/54.5
| Net/Gross weight | kg | 23.8/29.5 | 32.2/39 | 32.2/39.4 | 4.2/1.5 | 4.2/1.5
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | ODΦ25mm | ODΦ25mm
Drainage water pipe diameter |  | mm | ODΦ25 | ODΦ25 | ODΦ25 | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4")
Refrigerant piping | Liquid side/ Gas side | mm | Φ6.35/Φ12.7(1/4"/1/2") | Φ9.52/Φ15.9(3/8"/5/8") | Φ9.52/Φ19(3/8"/3/4") | wired control | wired control
Controller |  |  | wired control | wired control | wired control | 17~30 | 17~30
Room temperature | Cooling | ℃ | 17～32 | 17～32 | 17～32 | 17~32 | 17~32
| Heating | ℃ | 0～30 | 0～30 | 0～30 | 0~30 | 0~30
Qty’per 20’ /40’ /40'HQ |  | Indoor | 120/264/297 | 77/161/184 | 77/161/184 | 62/130/149 | 62/130/149
Remarks:1.The above design and specifications are subject to change without prior notice for product improvement.
Note on A26: 何桂敏: external static pressure

## HSP DUCT
NEW IDU&ODU
Indoor model |  |  | KSTR140HFAN3 | KSTR176HFAN3
Outdoor model |  |  | KSUT140HFAN3 | KSUT176HFAN3
Power supply |  | V,Hz,Ph | 380~415,50,3 | 380~415,50,3
Cooling | Capacity | Btu/h | 48000 | 55000
|  |  | 14.068 | 16.1196
| Input | W | 5750 | 6590
| Current | A | 9.4 | 11.1
| EER | W/W | 2.45 | 2.45
Heating | Capacity | Btu/h | 55000 | 60000
|  |  | 16.1196 | 17.585
| Input | W | 4815 | 5730
| Current | A | 8.3 | 10.2
| COP | W/W | 3.35 | 3.07
Indoor fan motor | Model |  | YKSS-210-4-2 | YKSS-210-4-2
| Qty |  | 1 | 1
| Input | W | 430.0 | 430.0
| Capacitor | uF | 10 | 10
| Speed(Hi/Med/Lo) | r/min | 790/715/620/540 | 790/715/620/540
Indoor coil | Number of rows |  | 3.0 | 3.0
| Tube pitch(a)*row pitch(b) | mm | 21x13.37 | 21x13.37
| Fin spacing | mm | 1.3 | 1.3
| Fin type |  | Hydrophilic aluminum(Golden) | Hydrophilic aluminum(Golden)
| Tube outside dia.and type | mm | Φ7,Inner groove tube | Φ7,Inner groove tube
| Coil length×height×width | mm | 1055*357*40.11 | 1055*357*40.11
| Number of circuits |  | 8 | 8
Indoor air flow (Hi/Med/Lo) |  | m3/h | 2650/1850/1450 | 2650/1850/1450
ESP | Rated | Pa | 50 | 50
| Range | Pa | 0-200 | 0-200
Indoor noise level (Hi/Med/Lo) |  | dB(A) | 50.5/45/42 | 50.5/45/42
Throttle type |  |  | 1200x625x380 | 1200x625x380
Indoor unit | Dimension (WxDxH) | mm | 1485x675x460 | 1485x675x460
| Packing(WxDxH) | mm | 52.1/60.4 | 52.2/60.2
| Net/Gross weight | kg | 4.2/1.5 | 4.2/1.5
Design pressure |  | MPa | ODΦ25mm | ODΦ25mm
Drainage water pipe diameter |  | mm | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4")
Refrigerant piping | Liquid side/ Gas side | mm | wired control | wired control
Controller |  |  | 17~30 | 17~30
Room temperature | Cooling | ℃ | 17~32 | 17~32
| Heating | ℃ | 0~30 | 0~30
Qty’per 20’ /40’ /40'HQ |  | Indoor | 59/124/125 | 59/124/125
Remarks:1.The above design and specifications are subject to change without prior notice for product improvement.
Note on A28: 何桂敏: external static pressure

## ON OFF UNIVERSAL OUTDOOR
Model |  |  | KSUT35HFAN1 | KSUT53HFAN1 | KSUT70HFAN1 | KSUR105HFAN3 | KSUT140HFAN3 | KSUT176HFAN3
Power supply |  | V,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3 | 380~415,50,3
Max. input consumption |  | W | 1650 | 2950 | 3450 | 4250 | 6300 | 7500
Max. input current |  | A | 8 | 15 | 18 | 7 | 11 | 12.6
Compressor | Model |  | ASM140V1VFT | PA215M2AS-7KTL6 | PA291X3CS-4MTM1 | ATQ420Y1TMT | C-SBN373H8D | C-SBN453H8D
| Type |  | ROTARY | ROTARY | ROTARY | ROTARY | Scroll | Scroll
| Brand |  | GMCC | GMCC | GMCC | GMCC | Panasonic | Panasonic
| Capacity | Btu/h | 13853 | 21308 | 24669 | 35690 | 48109 | 55957
| Input | W | 955 | 1530 | 2540 | 3430 | 4750 | 5750
| Rated current(RLA) | A | 4.35 | 6.9 | 12.25 | 6.1 | 8.22 | 9.77
| Locked rotor Amp(LRA) | A | 25 | 38 | 59 | 36 | 66 | 67
| Thermal protector position |  | Internal | Internal | Internal | Internal | Internal | Internal
| Capacitor | μF | 35 | 50 | 60 | ― | ― | ―
| Refrigerant oil | ml | ESTER OIL VG74/350 | ESTEL OIL VG74/620 | ESTER OIL VG74 · 950 | ESTER OIL VG74 1200CC | FV68S 1700 | FV68S 1700
Outdoor fan motor | Model |  | YKT-32-6-203L | YKT-48-6-206 | YKT-75-6-200L | YKS-190-6-21L | YKT-65-6-34L | YKT-65-6-34L
| Old Model |  | ― | ― | ― | ― | YDK65-6F(B) | YDK65-6F(B)
| Qty |  | 1 | 1 | 1 | 1 | 2 | 2
| Input | W | 72.5 | 104 | 144 | 293 | 162 | 162
| Capacitor | μF | 2.5 | 3.0 | 3.0 | 10 | 3.5 | 3.5
| Speed | r/min | 850/750 | 880/750 | 860/760 | 850/770 | 765 | 765
Outdoor coil | Number of rows |  | 2 | 2 | 2 | 2.0 | 2 | 2
| Tube pitch(a)* row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37 | 25.4x22 | 21x22 | 21x22
| Fin spacing | mm | 1.4 | 1.4 | 1.2 | 1.3 | 1.3 | 1.3
| Fin type |  | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminium(Golden) | Hydrophilic aluminum(Golden) | Hydrophilic aluminum(Golden)
| Tube outside dia.and type | mm | Φ7,innergroove tube | Φ7,innergroove tube | Φ7,innergroove tube | Φ9.52,innergroove tube | Ф7,Inner groove tube | Ф7,Inner groove tube
| Coil length * height * width | mm | 755x504x26.74 | 755x504x26.74 | 730x651x26.74 | 995x762x44 | 830*630*22+795*630*22 | 830*22*630+795*22*630
| Number of circuits |  | 4 | 4 | 6 | 4 | 8 | 8
Outdoor noise level (sound pressure) |  | dB(A) | 56 | 62 | 62 | 63 | 63 | 63.3
Outdoor air flow |  | m3/h | 1800 | 2000 | 2800 | 3800 | 6000 | 6000
Throttle type |  |  | capillary | capillary | Throttle Valve | Throttle valve | Throttle valve | Throttle valve
Outdoor unit | Dimension(WxDxH) | mm | 770x300x555 | 770x300x555 | 845x363x702 | 946x410x810 | 900x350x1170 | 900x350x1170
| Packing(WxDxH) | mm | 900x345x595 | 900x348x625 | 965x395x765 | 1090x500x875 | 1032x443x1307 | 1032x443x1307
| Net/Gross weight | kg | 32/34.5 | 36.5/39.7 | 52.7/56.1 | 74.4/78.9 | 98.6/109.3 | 99.7/111.2
Refrigerant type/Quantity | Type |  | R410A | R410A | R410A | R410A | R410A | R410A
| Charged volume | kg | 1.0 | 1.5 | 1.8 | 2.85 | 3.3 | 3.3
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5
Refrigerant piping | Liquid side/ Gas side | mm(inch) | Φ6.35/Φ12.7(1/4"/1/2") | Φ6.35/Φ12.7(1/4"/1/2") | Φ9.52Φ15.9(3/8"/5/8") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4") | Φ9.52/Φ19(3/8"/3/4")
| Max. pipe length | m | 15 | 25 | 25 | 30 | 50 | 50
| Max. difference in level | m | 8 | 15 | 15 | 20 | 30 | 30
Ambient temperature | Cooling | ℃ | 18-43 | 18-43 | 18-43 | 18～43 | 18-43 | -15-43
| Heating | ℃ | -7-24 | -7-24 | -7-24 | -7～24 | -7-24 | -7-24
Qty’per 20’ /40’ /40'HQ |  | Outdoor unit | 166/344/344 | 123/258/344 | 102/216/216 | 44/96/142 | 27/57/108 | 27/57/108
Remarks:1.The above design and specifications are subject to change without prior notice for product improvement.